	
	
	塔里木石化大化肥项目
	04088-06000-IN11
	2版

	
	
	熔融尿素装置
	第
	87
	页
	共
	180
	页



	编制 
	        
	校核 
	            
	审核
	          
	 日期
	



	 
	
	 仪表名称       
	工业电导仪
	
	

	
	
	 仪表位号      
	AT-1002
	AT-1004
	AT-1005

	
	
	 数    量       
	1
	1
	1

	
	
	 采样点设备或管道号  
	6”-PC413-31C
	6”-LC801-11E
	24”-LS801-11E

	
	
	 设备或管道规格和材料 
	
	
	

	
	
	    
	
	
	

	操
	  
	 介质名称或组分％ 
	H2O
	H2O
	低压蒸汽

	作
	
	 温    度         ℃
	50
	120
	147

	条
	
	 压    力         MPa
	0.6
	0.1
	0.34

	件
	
	 操作状态下密度   kg/m3
	988
	943
	2.4

	
	
	操作状态下粘度   mPa.s
	
	
	

	被
	
	 名称/单位       
	电导率 (s / cm
	电导率 (s / cm
	电导率 (s / cm

	测
	
	 最    大    
	
	
	

	参
	
	 正    常      
	20
	20
	20

	数
	
	 最    小     
	
	
	

	
	
	 测量范围    
	0~100 (s / cm
	0~100 (s / cm
	0~100 (s / cm

	
	
	 精度等级      
	(0.50%
	(0.50%
	(0.50%

	
	
	 型    号       
	
	
	

	传
	
	 电极型式 
	 MACROBUTTON CheckIt ( PH电极 MACROBUTTON UncheckIt (接触式
	 MACROBUTTON CheckIt ( PH电极 MACROBUTTON UncheckIt (接触式
	 MACROBUTTON CheckIt ( PH电极 MACROBUTTON UncheckIt (接触式

	
	
	 电极材料       
	316LSS
	316LSS
	316LSS

	感
	
	 与介质接触部件材料
	316LSS
	316LSS
	316LSS

	
	
	
	
	
	

	器
	
	 电气连接     
	 MACROBUTTON CheckIt (Pg13.5   MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt (Pg13.5   MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt (Pg13.5   MACROBUTTON CheckIt (

	
	
	 插入长度         mm
	 MACROBUTTON CheckIt ( 120   MACROBUTTON CheckIt (360   MACROBUTTON UncheckIt (56
	 MACROBUTTON CheckIt ( 120   MACROBUTTON CheckIt (360   MACROBUTTON UncheckIt (56
	 MACROBUTTON CheckIt ( 120   MACROBUTTON CheckIt (360   MACROBUTTON UncheckIt (56

	
	
	 温度补偿      
	 MACROBUTTON UncheckIt (有    MACROBUTTON UncheckIt ( MACROBUTTON CheckIt (Pt100 
	 MACROBUTTON UncheckIt (有    MACROBUTTON CheckIt (Pt100 
	 MACROBUTTON UncheckIt (有    MACROBUTTON CheckIt (Pt100 

	
	
	 型    号      
	
	
	

	
	
	 安装方式    
	 MACROBUTTON UncheckIt (管装  MACROBUTTON CheckIt (墙装  MACROBUTTON CheckIt (
	 MACROBUTTON UncheckIt (管装  MACROBUTTON CheckIt (墙装  MACROBUTTON CheckIt (
	 MACROBUTTON UncheckIt (管装  MACROBUTTON CheckIt (墙装  MACROBUTTON CheckIt (

	变
	
	 供电电源     
	24VDC
	24VDC
	24VDC

	
	
	 输出信号     
	 MACROBUTTON UncheckIt (4~20mA二线制
	 MACROBUTTON UncheckIt (4~20mA二线制
	 MACROBUTTON UncheckIt (4~20mA二线制

	送
	
	 指 示 器  
	 MACROBUTTON CheckIt (指针式  MACROBUTTON UncheckIt (数字式
	 MACROBUTTON CheckIt (指针式  MACROBUTTON UncheckIt (数字式
	 MACROBUTTON CheckIt (指针式  MACROBUTTON UncheckIt (数字式

	
	
	 型    式      
	 MACROBUTTON CheckIt (继电器 MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt (继电器 MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt (继电器 MACROBUTTON CheckIt (

	器
	开
	 数    量     
	 MACROBUTTON CheckIt (单    MACROBUTTON CheckIt (双    MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt (单    MACROBUTTON CheckIt (双    MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt (单    MACROBUTTON CheckIt (双    MACROBUTTON CheckIt (

	
	关
	 作用形式       
	 MACROBUTTON CheckIt (SPDT  MACROBUTTON CheckIt ( DPDT MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt (SPDT  MACROBUTTON CheckIt ( DPDT MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt (SPDT  MACROBUTTON CheckIt ( DPDT MACROBUTTON CheckIt (

	
	
	 接点容量      
	
	
	

	连
	
	 电气连接     
	 MACROBUTTON CheckIt (Pg13.5   MACROBUTTON UncheckIt (1/2”NPT
	 MACROBUTTON CheckIt (Pg13.5   MACROBUTTON UncheckIt (1/2”NPT
	 MACROBUTTON CheckIt (Pg13.5   MACROBUTTON UncheckIt (1/2”NPT

	接
	
	 过程连接     
	3/4”NPT 
	3/4”NPT
	3/4”NPT 

	外
	
	 防护等级     
	 MACROBUTTON UncheckIt ( IP65    MACROBUTTON CheckIt (  
	 MACROBUTTON UncheckIt ( IP65    MACROBUTTON CheckIt (  
	 MACROBUTTON UncheckIt ( IP65    MACROBUTTON CheckIt (  

	壳
	
	 防爆类别      
	EExiaIICT4
	EExiaIICT4
	EExiaIICT4

	附
	
	 流通式安装件   
	 MACROBUTTON UncheckIt (带      MACROBUTTON CheckIt ( 
	 MACROBUTTON UncheckIt (带      MACROBUTTON CheckIt ( 
	 MACROBUTTON UncheckIt (带      MACROBUTTON CheckIt ( 

	件
	
	 专用电缆       
	 MACROBUTTON UncheckIt ( 5 m
	 MACROBUTTON UncheckIt ( 5 m
	 MACROBUTTON UncheckIt ( 5 m

	
	
	 用    途       
	出界区净化水电导率
	V-110蒸汽冷凝液
	来自E-105蒸汽电导率 

	
	
	
	
	电导率
	

	
	
	 型    号      
	
	
	

	
	
	
	
	
	

	
	
	 备    注     
	变送器带2”管装安装支架.
	变送器带2”管装安装支架
	变送器带2”管装安装支架

	
	
	
	P53
	P54
	P44

	备注: 1. 禁铜及铜合金.

	     2. 带3/4”NPT(F)三通接头. 接头材质为316LSS.

	

	

	
	
	 仪表名称       
	工业电导仪
	
	

	
	
	 仪表位号      
	AT-1006
	
	

	
	
	 数    量       
	1
	
	

	
	
	 采样点设备或管道号  
	6”-MC802-13B
	
	

	
	
	 设备或管道规格和材料 
	
	
	

	
	
	    
	
	
	

	操
	  
	 介质名称或组分％ 
	H2O
	
	

	作
	
	 温    度         ℃
	219
	
	

	条
	
	 压    力         MPa
	2.17
	
	

	件
	
	 操作状态下密度   kg/m3
	842
	
	

	
	
	操作状态下粘度   mPa.s
	
	
	

	被
	
	 名称/单位       
	电导率 (s / cm
	
	

	测
	
	 最    大    
	
	
	

	参
	
	 正    常      
	20
	
	

	数
	
	 最    小     
	
	
	

	
	
	 测量范围    
	0~100 (s / cm
	
	

	
	
	 精度等级      
	(0.50%
	
	

	
	
	 型    号       
	
	
	

	传
	
	 电极型式(*注2) 
	 MACROBUTTON CheckIt ( PH电极 MACROBUTTON UncheckIt (接触式
	 MACROBUTTON CheckIt ( PH电极 MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt ( PH电极 MACROBUTTON CheckIt (

	
	
	 电极材料       
	316LSS
	
	

	感
	
	 与介质接触部件材料
	316LSS
	
	

	
	
	
	
	
	

	器
	
	 电气连接     
	 MACROBUTTON CheckIt (Pg13.5   MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt (Pg13.5   MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt (Pg13.5   MACROBUTTON CheckIt (

	
	
	 插入长度         mm
	 MACROBUTTON CheckIt ( 120   MACROBUTTON CheckIt (360  MACROBUTTON UncheckIt (56
	 MACROBUTTON CheckIt ( 120   MACROBUTTON CheckIt (360   MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt ( 120   MACROBUTTON CheckIt (360   MACROBUTTON CheckIt (

	
	
	 温度补偿      
	 MACROBUTTON UncheckIt (有    MACROBUTTON CheckIt (Pt100 
	 MACROBUTTON CheckIt (有    MACROBUTTON CheckIt (Pt100 
	 MACROBUTTON CheckIt (有    MACROBUTTON CheckIt (Pt100 

	
	
	 型    号      
	
	
	

	
	
	 安装方式    
	 MACROBUTTON UncheckIt (管装  MACROBUTTON CheckIt (墙装  MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt (管装  MACROBUTTON CheckIt (墙装  MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt (管装  MACROBUTTON CheckIt (墙装  MACROBUTTON CheckIt (

	变
	
	 供电电源     
	24VDC
	
	

	
	
	 输出信号     
	 MACROBUTTON UncheckIt (4~20mA二线制
	 MACROBUTTON CheckIt ( 4~20mA      MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt ( 4~20mA      MACROBUTTON CheckIt (

	送
	
	 指 示 器  
	 MACROBUTTON CheckIt (指针式  MACROBUTTON UncheckIt (数字式
	 MACROBUTTON CheckIt (指针式 MACROBUTTON CheckIt (数字式
	 MACROBUTTON CheckIt (指针式 MACROBUTTON CheckIt (数字式

	
	
	 型    式      
	 MACROBUTTON CheckIt (继电器 MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt (继电器 MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt (继电器 MACROBUTTON CheckIt (

	器
	开
	 数    量     
	 MACROBUTTON CheckIt (单    MACROBUTTON CheckIt (双    MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt (单    MACROBUTTON CheckIt (双    MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt (单    MACROBUTTON CheckIt (双    MACROBUTTON CheckIt (

	
	关
	 作用形式       
	 MACROBUTTON CheckIt (SPDT  MACROBUTTON CheckIt ( DPDT MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt (SPDT  MACROBUTTON CheckIt ( DPDT MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt (SPDT  MACROBUTTON CheckIt ( DPDT MACROBUTTON CheckIt (

	
	
	 接点容量      
	
	
	

	连
	
	 电气连接     
	 MACROBUTTON CheckIt (Pg13.5   MACROBUTTON UncheckIt (1/2”NPT
	 MACROBUTTON CheckIt (Pg13.5   MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt (Pg13.5   MACROBUTTON CheckIt (

	接
	
	 过程连接     
	3/4”NPT 
	 MACROBUTTON CheckIt (Pg13.5   MACROBUTTON CheckIt (   
	 MACROBUTTON CheckIt (Pg13.5   MACROBUTTON CheckIt (   

	外
	
	 防护等级     
	 MACROBUTTON UncheckIt ( IP65    MACROBUTTON CheckIt (  
	 MACROBUTTON CheckIt ( IP65    MACROBUTTON CheckIt (    
	 MACROBUTTON CheckIt ( IP65    MACROBUTTON CheckIt (   

	壳
	
	 防爆类别      
	EExiaIICT4
	
	

	附
	
	 流通式安装件   
	 MACROBUTTON UncheckIt (带      MACROBUTTON CheckIt ( 
	 MACROBUTTON CheckIt (带      MACROBUTTON CheckIt (
	 MACROBUTTON CheckIt (带      MACROBUTTON CheckIt (  

	件
	
	 专用电缆       
	 MACROBUTTON UncheckIt ( 5m
	 MACROBUTTON CheckIt (       m
	 MACROBUTTON CheckIt (       m

	
	
	 用    途       
	V-109蒸汽冷凝液 
	
	

	
	
	
	电导率
	
	

	
	
	 型    号      
	
	
	

	
	
	
	
	
	

	
	
	 备    注     
	变送器带2”管装安装支架
	
	

	
	
	
	P43
	
	

	备注: 1. 禁铜及铜合金.

	     2. 带3/4”NPT(F)三通接头. 接头材质为316LSS.

	









